Copyright 2002, The American Institute of Architects (AIA)

SECTION 264113 - LIGHTNING PROTECTION

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

SUMMARY

This Section includes lightning protection for building(s).

DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

NRTL:  National recognized testing laboratory.

SUBMITTALS

Product Data:  For all equipment utilized in the system including but not limited to air terminals and mounting accessories, connectors, bonds, conductors fasteners and grounds.

Shop Drawings:  Detail lightning protection system, including air-terminal locations, conductor routing and connections, and bonding and grounding provisions.  Include indications for use of raceway, and data on how concealment requirements will be met.

Qualification data for firms and persons specified in "Quality Assurance" Article to demonstrate their capabilities and experience.  Include data on listing or certification by an NRTL.

Retain first paragraph below for air terminals mounted on single-ply membrane roofing.

Certification, signed by Contractor, that roof adhesive for air terminals is approved by manufacturers of both the terminal assembly and the single-ply membrane roofing material.

Field inspection reports indicating compliance with specified requirements.

QUALITY ASSURANCE

Installer Qualifications:  Engage an experienced installer who is certified by a NRTL.

Listing and Labeling:  As defined in NFPA 780, "Definitions" Article and UL 96.

COORDINATION

Coordinate installation of lightning protection with installation of other building systems and components, including electrical wiring, supporting structures and building materials, metal bodies requiring bonding to lightning protection components, and building finishes.

Coordinate installation of air terminals attached to roof systems with roofing manufacturer and Installer.

PRODUCTS

MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

National Lightning Protection Corporation (800-628-2816)

Harger Lightning Protection (800-842-7437)

Independent Lightning Protection (800-

LIGHTNING PROTECTION SYSTEM COMPONENTS

Comply with UL 96.

Select material classification of NFPA 780; see Table 2 in the Evaluations.  NFPA requires Class II air terminals to be solid.

See Editing Instruction No. 2 in the Evaluations.  Specified standards stipulate minimum size requirements for components, depending on selected metal and class of building.  If components larger than minimum size are desired, add appropriate requirements here.

Air Terminals:  NFPA Class [I] [II], [aluminum] [copper], [solid], unless otherwise indicated.  The air terminals shall be OSHA recognized impalement resistant air terminals equal to National Lightning Protections’ Flathead air terminal.

Delete subparagraph below or revise to suit Project.

Single-Membrane, Roof-Mounting Air Terminal Bases:  Designed for single-membrane roof materials.

Conductors:  Shall be stranded or solid to comply with UL 96 requirements.

No crimp conductor connections or stamped bases, bond plates, connectors or components of any of the systems parts and pieces will be allowed with the exception of fasteners.

Grounding per UL 96A.

EXECUTION

INSTALLATION

Edit first paragraph below to indicate which standards apply.  Retain UL if UL Master Label or LPI certification is specified, and NFPA if the most stringent or comprehensive requirements are needed.

Install lightning protection components and systems according to UL 96A.

Install conductors with direct paths from air terminals to ground connections.  Avoid sharp bends and narrow loops.

Conceal the following conductors:

Retain some or all of five subparagraphs below depending on degree of concealment desired for lightning protection components.  If deleting all five, there will be no restrictions on exposed conductors.

Down conductors

Interior conductors.

Take digital pictures of all lightning protection components before concealment and include copies to the NRTL and the Engineer.

Exothermic-welded connections are considered more permanent than crimped or bolted connections.  If exothermic-welded connections are desired, retain paragraph below.  Edit if single-ply membrane roofing is not used or if exothermic connections are only required in underground portions of system.

Cable Connections:  Use UL listed lightning protection connections for all conductor splices and connections between conductors and other components.

Retain paragraph below for single-ply membrane roofing.

Air Terminals on Single-Ply Membrane Roofing:  Comply with adhesive manufacturer's written instructions.

Delete two paragraphs and associated subparagraphs below if NFPA 780 compliance is specified; retain if specifying bonding requirements that exceed minimum UL 96A requirements.  See Editing Instruction No. 3 in the Evaluations.  Coordinate with Drawings for counterpoise requirements, if any.

Bond extremities of vertical metal bodies exceeding 60 feet in length to lightning protection components.

If a counterpoise is required:

Bond ground terminals to counterpoise conductor.

Bond grounded metal bodies on building within 6 feet of ground to counterpoise conductor.

Bond grounded metal bodies on building within 6 feet of roof to interconnecting loop at eave level or above.

CORROSION PROTECTION

Do not combine materials that can form an electrolytic couple that will accelerate corrosion in the presence of moisture unless moisture is permanently excluded from junction of such materials.

Use conductors with protective coatings where conditions would cause deterioration or corrosion of conductors.

FIELD QUALITY CONTROL

Edit this Article to specify inspections for UL Master Label or LPI certification.  See Evaluations.

Retain one of two paragraphs below.

UL Inspection:  Provide an inspection as required to obtain a UL Inspection Certificate for the system.  A written letter of compliance from the installer or manufacturer does not comply with this requirement.

END OF SECTION 13100